GENERIC SPECIFICATION

IPS Controller 5000

Mechanical and Electrical Details

The integrated pumping system (IPS) pump logic controller shall be Armstrong IPS Controller 5000. The IPS pump logic controller shall be specifically designed for the control of multiple pump HVAC hydronic and/or chilled water systems that involve up to 4 variable speed, or fixed speed pumps in parallel, staged, sequenced, and standby configurations. The IPS pump logic controller shall allow field adjustments of control parameters as described below.

The IPS controller shall be capable of accepting and processing appropriate signals (DP, Temperature, or Flow) for the following dedicated terminal blocks:

1.	5 analog inputs (AI) for zone DP, Temperature, or Flow transmitter signals 4-20 mA

2.	1 AI for DP transmitter or flow sensor run-out protection,

3.	4 digital inputs (DI), one per pump, DP switch

4.	1 DI for remote connection for start/stop

5.	4 DIs, one per pump for fault signal,

6.	4 DIs, one per VFD for fault signal,

7.	1 DI for alarm silencer,

8.	4 Analog Output (AO), one per VFD for speed signal,

9.	4 digital outputs (DO), one per pump/vfd for on/off signal,

10.	3 DO for alarms:

a.	Pump/motor/VFD alarm,

b.	DP transmitter alarm,

c.	General system alarm

11.	4 DO, one per VFD for automatic bypass activation,

12.	2 or 4 AI, for motor temperature probes (PT100 or NTC),

13.	1 serial port for communication with the BMS,

14.	1 serial port for communication with the VFDs,

15.	1 terminal block for power supply 230V/1/50Hz

The IPS pump logic controller shall have an internal circuit breaker. The logic controller shall be based on Flash style memory, older style EEPROM style memory is unacceptable.

The IPS controller shall include a 5.7” back-lit touch-screen for all necessary user interface functions. Keypad based interfaces, LCD readouts, and LED displays will not be accepted. The IPS pump logic controller shall perform online self-diagnostic testing of the CPU(s), RAM, and flash memory. No data shall be lost during power supply interruptions.

The IPS pump logic controller shall have an IP54 rated cabinet. The IPS controller shall have two levels of password security, one level for field adjustable parameters, a second for factory/commissioning setup parameters.

The IPS complies with the requirements for the following harmonised standards:

- Safety requirements for Low Voltage Switchgear & Controlgear Assemblies; BS EN 60439-1 (1999)

- Electromagnetic Compatibility (EMC) Part 6-3: Generic Standard;

Electromagnetic Compatibility (EMC) Emission Standard for Residential,

Commercial & Light-Industrial Environments.

BS EN 61326 Industrial, BS EN 55022, BS EN 55011, BS EN 61000-6-3 (2007)

- Electromagnetic Compatibility (EMC) Part 6-2 : Generic Standard;

Electromagnetic Compatibility (EMC) Immunity Standard for Industrial Environments.

BS EN 61326 Industrial, BS EN 61000-6-2 (2005)

The IPS conforms with the provisions of the following European Directives:

- Low Voltage Directive: 2006/95/EC

including all current amendments thereof.

- Electromagnetic Compatibility (EMC) Directive: 2004/108/EC

including all current amendments thereof.

Performance and Operating Logic

The IPS pump logic controller shall determine the most efficient combination of operating pumps, and pump operating speed based on the zone DP, Temperature, or Flow sensor signals. The IPS pump logic controller shall respond to the most dissatisfied zone by increasing either, the number of operating pumps, or the pump speed. In the case where all zones are satisfied the IPS pump logic controller shall respond by decreasing either, the number of operating pumps, or the pump speed so as to optimize the energy efficiency of the pumping operation while meeting system demand. The IPS pump logic controller shall continuously monitor all zone signals to determine an active control zone. Use of a multi-plexer for multiple sensor inputs is not acceptable. To prevent unnecessary changes to the operating pump speed, to become the active control zone, the candidate zone must have a greater error from set-point than the current active control zone for greater than 5 minutes. This transition delay period, 5 minutes, shall be a field adjustable parameter that can be altered by the password protected users.

The IPS pump logic controller shall sequence the pumps based on a field adjustable interval of operating hours with a “bump-less” transfer algorithm. The logic controller shall incorporate embedded logic to prevent hunting, pump flow surge, and motor overloading. The logic shall incorporate an adjustable PID control loop. PID control at the VFD is not acceptable.

Should one vfd/pump/by-pass unit fail, the appropriate alarm signal shall be activated. In the place of the failed assembly, a standby vfd/pump unit shall be operated in variable speed mode. If the system demand is too great with the standby on VFD the IPS pump logic controller shall send an automatic by-pass signal to each VFD / by-pass assembly to operate in by-pass.

The IPS controller shall have hand-off-automatic (H-O-A) control and should provide the option for a remote on/off signal from a single dry type relay, or BMS communication signal.

The IPS pump logic controller shall provide a data-logging feature including alarms, and events (adjustment to system parameters). The IPS pump logic controller shall offer the option for expanded memory of 4 megabytes for a rolling record of system parameters at 10 second intervals, with a time stamp.

The IPS pump logic controller shall be self-prompting. All messages shall be displayed in plain English. The operator interface shall have; Multi-fault memory and recall, On-screen help functions, and separate user screens for:

- Zone setups (including calibration of DP/T/Flow sensor range)

- Pump configuration

- Design set-point and end of curve data

- Alarm history and event review

- Display of zone status, pump status, system status

- Factory default / commissioning setup data

The IPS controller shall be capable of serial communications with Modbus, LonWorks, Trend, and Metasys protocols. The IPS controller shall offer the option of gateways for both BACnet and TCP/IP protocol connection for communication over the internet.

The IPS pump logic controller shall automatically disable any zone DP/T/Flow signals that are not within limits and alert the operator of a possible transmitter failure. Should system failure be detected the pump speed will default to a pre-defined percent of full speed (factory default loaded as 90% of full speed). The IPS pump logic controller shall have a minimum speed limit entered as a field adjustable parameter, factory loaded default set to 30% of

full speed.