TYPICAL SPECIFICATION

ARMEX II

Specification for AM2-2/35 duty/standby pump control unit with AVG200 expansion vessel, RPZ valve Fillset and DE60 liter buffer vessel.

AM2-2/35

Sealed system pressure control and degassing unit with automatic water make up. Duty and standby pump with soft start. Pressure control valve for each pump and solenoid operated pressure control valves. Automatic degassing on a programmable and timed basis. IP54 enclosure control panel incorporating two programmable volt free contacts and an RS485 serial link, LED read out of pressure and vessel % full in clear text. Graphical display of water make up, overflow and pump operation. Hand /off/auto switch. Fault memory in chronological order. Parameter setting. Eight languages. Suitable for glycol solutions up to 50% concentration. Wired for a 1/50/230 supply.

Armex II controller fitted with two volt free contacts (common alarm and low water level in AVG vessel).

AVG200

Steel expansion tank fitted with replaceable EPDM diaphragm, load pressure cell, air release valve to release free air from within the diaphragm and air vent to allow the vessel to remain at atmospheric pressure.

1" connection kit to connect single pump sets to AVG vessels up to AVG1000 (740D) with shut off valve and screwed connections.

RPZ Valve Fillset

Fill set with RPZ valve ensuring category 4 separations with shut off valves. WRAS approved.

Buffer vessel

DE60 buffer vessel, supplied loose for systems up to 10 bar.